## GENSETS

## PC-12-08

SUBJECT:	Fuel Caps Not Properly Vented

MODELS AFFECTED:	G8 through G575

SYMPTOMS:		Fuel leaking around fittings, over pressureization,

Excessive cap back pressure.

CAUSE:	Lack of proper tank ventilation

REMEDY:	Replace Fuel cap

Part # 85509222

ACTION:			Order cap and replace.

P/N 85509222

Dispose of original cap locally.

Warranty claims will be accepted until April 1, 2003 for part and freight.

Claims should refer to “campaign 02-2”.