## GENSETS

## PC-12-010

SUBJECT:	Fuel Leaks around Fuel Gauge.

MODELS AFFECTED:	G8 through G40

SYMPTOMS:		Fuel leaking around Gauge Base

CAUSE:	Improper seal

REMEDY:	Replace flange seal, and reseal per supplied instructions

ACTION:			Order seal and repair.

P/N 85490811 for seal, 85626364 for spacer if needed

And 85430007 for sealant

This is not a Campaign.