## GENSETS

## PC-12-12

Date 7-10-03

SUBJECT:	Module Four Cable Strain Reliefs

MODELS AFFECTED:	G50 through G575

SYMPTOMS:	Mod 4 can bus fault will appear on unit display and cause a

shut down

CAUSE:	Strain relief only offers one supporting screw, thus allowing cable to lose contact with the CB 12 and Can Bus

REMEDY:	Replace Strain Relief

Part # 85626638

ACTION:			Order Strain Relief and Replace.

P/N

Dispose of parts locally.

Warranty claims will be accepted until April 1, 2003 for parts, labor, and freight.

Claims should refer to “campaign 02-3”.