## GENSETS

## PC-12-14

Date 7-14-03

SUBJECT:	          Damaged wires & insulation exiting Alternator J Box

MODELS AFFECTED:	G20 through G40

SYMPTOMS:      Excessive wear or shorting of wiring exiting J box on the

Alternator

CAUSE:               Loose or improperly routed wire through J box

REMEDY:           Check wiring inside J box for proper fit and condition at each

1000 hrs,

ACTION:	    Secure and reroute all loose or rubbing wires in J box, with zip ties or

other proper mounting hardware. Replace any damaged wire, or any wire with damaged insulation.