## GENSETS 60HZ

## PC-12-16

Date 8-31-03

SUBJECT:	                              Correct Capacitor Replacement

MODELS AFFECTED:         L6-L8 Light towers

SYMPTOMS:	              Replacement parts for capacitor may not match OEM Capacitor

CAUSE:                                Production change

REMEDY:                           Follow instructions below

CAUTION!  USING CAPACITORS WITH TOO HIGH A UF. VALUE MAY RESULT IN FAILURE AND

DAMAGE TO THE GENERATOR.

When replacing capacitors on L6 or L8 light towers, care should be taken to prevent installation of capacitors with too high a

uF. Value.

L6 light towers should have one 70 uF, capacitor and L8 light towers should  Have one 100 UF or 2-50 uF  capacitors.

If you are replacing a capacitor on a generator that has two 50 uF capacitors, both

Capacitors should be removed and replaced with one 100 uF capacitor IR CPN 36883486.  The extra T5 and T8 wires should be removed or taped up.

The L6 capacitor is a 70uF and is IR CPN 36883478

NOTE:  When in doubt, consult qualified Ingersoll Rand Portable Power service for assistance (800-633-5206)