## GENSETS 60HZ

## PC-12-17

Date 12-19-03

SUBJECT:	                              Fuel Solenoid will not pull in on start

MODELS AFFECTED:         G25 thru G40 shipped prior to 12/01/03

SYMPTOMS:	              Unit will crank but not start

CAUSE:                                 Pump lever and Solenoid are not properly aligned

REMEDY:                             Order and install kit # 22354104, to replace fuel lever and wiring to  power solenoid

Claims will be accepted until 1-June-04 per campaign # 02-04, for the kit and .5hr

labor per machine