## GENSETS

## PC-12-19

Date 11-24-04

SUBJECT:	                          Incorrect Fuel Solenoid wiring

MODELS AFFECTED:        G25A-40A

SYMPTOMS:		              Unit will not start and or fuel solenoid will fail

CAUSE:	Incorrect wiring to fuel relay

REMEDY:	Rewire control wiring per instructions, supplied with this TSB

ACTION:			Make wiring changes per instructions

Warranty claims will be accepted until May 1, 2005 for parts, labor.

Claims should refer to “campaign 04-6”.